Customer Instructions for Completing the COVER form (DCG)

As per the Technical Interconnection Requirements (TIR), the COVER process shall apply to all distribution connected/connecting generator (DER) facilities that exceed 10 kW and impact Alectra Utilities Corporation’s distribution system.  The requirements of the COVER may vary depending on generation capacity and the connection requirements associated with upstream impacts dictated by the Customer Impact Assessment (CIA).

COVER PROCESS:

STAGE 1:  PLAN

Step 1:  Customer (Generator) Information

    - Complete Facility and Customer Contact Information of the COVER Form by completing the highlighted portions of Sections 1 & 2.

Step 2:  Identify the Tests that the Customer Intends to Conduct

    - Complete Highlighted portions (Legend columns) of Sections 3, where applicable

    - Complete Highlighted portions of Section 4 (Test Needed and Legend columns)

    - Complete Highlighted portions of Section 5 (Legend column), 6 (Legend column) and 7 (Legend column)

    - Submit commissioning plan to Alectra Utilities Corporation

Note:  The design review must be finalized prior to completing this step.

Step 3:  Alectra Utilities’ COVER Coordinator Review

    - Return COVER Form by email to the Alectra Stations Engineer

    - The COVER coordinator will review the proposed documents and respond to the acceptability of the proposed COVER/commissioning plan within 8 business days.

Note:  The commissioning plan review must be finalized prior to commencing testing for the next step. The COVER Coordinator approves the proposed COVER/commissioning plan by initialing page 5.

STAGE 2: PRE-ENERGIZATION

Step 4:  Completion of Testing and Resolution of all Comments

    - Complete all applicable testing in Sections 3, 4, 5 & 6.

    - Sign off the COVER, in section 6, by a Customer P.Eng Representative, and submit it to the Alectra Stations Engineer, ten (10) business days in advance of energization date.

    - The COVER Coordinator will review the certified COVER and recommend to the Controlling Authority (CA) for connection to the grid by signing section 6. The controlling authority will be Alectra Utilities System Control.

    - Section 7 testing can only proceed when all salient comments have been resolved and tests completed for Sections 3 to 6.

    - The customer will contact the Controlling Authority who will provide authorization to connect to the grid. The controlling authority will be Alectra Utilities’ System Control.

STAGE 3: POST-ENERGIZATION

Step 5:  Final Potential and On-load Checks

    - Complete and sign Section 7 when all parts of the COVER form are complete and submit it to the Alectra Stations Engineer (Note: online load readings and power factor performance test to be performed within ten (10) business days of placing station in service as generator.  Customer contacts Stations Engineer if constant power factor requirements can not be met.  Alectra Utilities will have 5 business days to review the issue).

    - Summary of testing results and certificates must be kept on file for a minimum period of 7 years by the Customer (as indicated by IESO Market Rules, Chp.4, 5.1.3). Alectra may require this information, on an exception basis. Alectra’s COVER Coordinator will distribute complete COVER to distribution list found on Page 11.

CLASSIFICATIONS:

CAE (Capacity Allocation Exempt) – A generation facility which is not a micro generation facility and which has a name-plate rated capacity:

(1) Less than or equal to 250 kW and connected to a less than 15 kV line

(2) Less than or equal to 500 kW and connected to a 15 kV or greater line

CAR (Capacity Allocation Required) – A generation facility which is not a micro generation facility and which has a name-plate rated capacity:

(1) Greater than 250 kW and connected to a less than 15 kV line

(2) Greater than 500 kW and connected to a 15 kV or greater line

#### Alectra Utilities Corporation

161 Cityview Boulevard

Vaughn, Ontario, L4H 0A9

CONFIRMATION OF VERIFICATION EVIDENCE REPORT (COVER)

[Distributed Energy Resources]

(Refer to Instructions Page)

| ##### Section 1 | ##### FACILITIES INFORMATION |  |  |
| --- | --- | --- | --- |
| ###### Name of Customer |  |  |  |
| ###### Name of Generator Facility |  |  |  |
| ###### Generator Address |  |  |  |
| ###### Proposed Energization Date |  |  |  |
| ###### OEB Generator License Number (if applicable) |  |  |  |
| ###### Supply Station and Feeder Designations |  | Alectra to provide |  |
| ##### Section 2 | ##### CONTACT INFORMATION |  |  |
| CUSTOMER CONTACT ALECTRA COVER COORDINATOR CONTACT |  |  |  |
| Print Name: Title: Date: Tel. #: Email: |  |  | Print Name: Alectra to provide Title: Alectra to provide Date: Alectra to provide Tel. # Alectra to provide Email: Alectra to provide |

| ##### Section 3 | ##### VERIFICATION-PROTECTION & CONTROL |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Legend: C = Confirm Results: P = Pass, F = Fail All Parts: N/A = Not Applicable |  | Legend | Results | Initials | Date mm/dd/yyyy | Note # |
| - Is commissioning in compliance with the submitted Commissioning plans? |  |  |  |  |  |  |
| - Are reviewed relay settings applied? |  |  |  |  |  |  |
| Confirm that the following protection systems, as applicable, have been verified to function as per the design: NOTE: Tests marked with an asterisks (*) require Hydro One staff coordination for the Hydro One owned Stations |  |  |  |  |  |  |
| Feeder Protection – All elements used to protect feeder |  |  |  |  |  |  |
| HV Breaker Failure Protection |  |  |  |  |  |  |
| LV Breaker Failure Protection |  |  |  |  |  |  |
| Transformer Differential Protection |  |  |  |  |  |  |
| Transformer Backup Protection |  |  |  |  |  |  |
| Under and Over Frequency |  |  |  |  |  |  |
| Under and Over Voltage |  |  |  |  |  |  |
| Other Anti-islanding Protection (in lieu of transfer trip) |  |  |  |  |  |  |
| Certified to CSA C22.3 (Most recent standard) / Bears certification mark (applicable to Inverter based DER) |  |  |  |  |  |  |
| Transfer Trip / Remote Trip * |  |  |  |  |  |  |
| DGEO (Generator End Open) * |  |  |  |  |  |  |
| Blocking Scheme Circuits * |  |  |  |  |  |  |
| Reverse Power for Generators |  |  |  |  |  |  |
| Reverse Power for Main Breaker |  |  |  |  |  |  |
| Gen. Protection that trip HV Sync Breakers |  |  |  |  |  |  |
| Instrument Transformer (eg. CTs + VTs, etc.) |  |  |  |  |  |  |
| Monitoring Equipment (eg. DFR, SER, etc.) |  |  |  |  |  |  |
| Other (Specify) |  |  |  |  |  |  |

| ##### Section 4 | ##### TELEMETRY TESTS BEFORE ENERGIZATION AT DISTRIBUTION CONNECTED GENERATOR |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Confirm the following SCADA telemetry quantities, where applicable Legend: C = Confirm; Results: P = Pass, F = Fail All Parts: N/A = Not Applicable |  | Legend | Results | Initials | Date mm/dd/yyyy | Note # |
| MW Flows and Directions |  |  |  |  |  |  |
| MVAR Flow and Directions |  |  |  |  |  |  |
| Phase to Phase or Phase to Neutral Voltages |  |  |  |  |  |  |
| Three Phase Currents |  |  |  |  |  |  |
| HV switchers/HV breakers/Bus Tie Breakers Open/Close Status |  |  |  |  |  |  |
| LV Breakers/Interrupters/Switchers, Open/Close Status |  |  |  |  |  |  |
| Protection Alarms (such as TT receive from Alectra Utilities, DGEO send, failure of interface protection, breaker failure, connection status) |  |  |  |  |  |  |
| Connect Permission Status |  |  |  |  |  |  |
| Generator Shutdown Command (Disconnect) and Block Connect |  |  |  |  |  |  |
| Allow Generator Connect |  |  |  |  |  |  |
| Other (specify) |  |  |  |  |  |  |

| ##### Section 5 |  | ##### CONFIRMATION OF VERIFICATION-POWER EQUIPMENT |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | Legend: C = Confirm, W = Witness Result: P = Pass, F = Fail All Parts: N/A = Not Applicable Note, some of the following verification may require Alectra staff witnessing. |  | Legend | Result | Initial | Date mm/dd/yyyy | Note # |
|  | - Verify the HV disconnect switches/circuit switchers are suitable as an isolation point per Utility Work Protection Code? NOTE: Any new or future modifications to the isolation device(s) used to provide supporting guarantees to Alectra staff under the Utility Work Protection Code. |  | C |  |  |  |  |
|  | - Name of Alectra Staff Witnessing HV Disconnect (if applicable) |  | Name: |  |  |  |  |
|  | - Confirm correct operation of the HV disconnect switches/circuit switchers/breakers |  |  |  |  |  |  |
|  | - Is closing time within manufacturer’s specification? |  |  |  |  |  |  |
|  | - Is opening time within manufacturer’s specification? |  |  |  |  |  |  |
|  | - Are the specified HV surge arrestors installed? |  |  |  |  |  |  |
|  | - Confirm the power transformer Doble test results are within specification |  |  |  |  |  |  |
|  | - Confirm power transformers connected correctly as per the design. |  |  |  |  |  |  |
|  | - Confirm the DC system installed (ie battery, charger, dc panel, dc monitoring). Verified? |  |  |  |  |  |  |
|  | - Does the HV equipment (ie, disconnect switches, circuit switchers, breakers, CVTs, CTs) have the appropriate voltage class and current ratings as per the submitted Single Line Diagram? |  |  |  |  |  |  |
|  | - Other (specify) |  |  |  |  |  |  |

| ##### Section 6 | ##### ELECTRICAL SAFETY |  |  |
| --- | --- | --- | --- |
| Legend: SD = Supporting Document, N/A = Not Applicable |  | Legend | Date mm/dd/yyyy |
| - Prior to energizing any new or modified customer or generator facilities, Electrical Safety Authority (ESA) must provide a Temporary Connection Authorization (Ontario Electrical Safety Code Article 2-014). Attach document. |  |  |  |
| - Prior to final in-service of new or modified customer or generator facilities, ESA must provide Connection Authorization (Code Article 2-012). Attach document. |  |  |  |
| - For those entities that are exempt under the ESA, the Customer shall provide a letter signed and sealed by a Professional Engineer registered in the province of Ontario, stating that Customer’s equipment was manufactured and installed in accordance with applicable regulations and relevant industry standards and practices prior to the Ready for Service Date Attach document. |  |  |  |

| Alectra’s COVER Coordinator approves the proposed checks, verifications, tests and notes submitted by the customer for the Plan Stage of the COVER*. | Alectra COVER Coordinator Initials |
| --- | --- |

NOTES:  (For Sections 3, 4, 5 & 6)

| #: | Comments: | Date Action Resolved: (dd/mm/yyyy) | CustomerInitials | COVER Coordinator Concurrence |
| --- | --- | --- | --- | --- |

| By signing* this form, the customer acknowledges that all required verifications specified under this COVER document have been completed and that the generator facility design and operation meets the minimum standards for generator facilities connected to a distribution system, as per the Distribution System Code and the generator holds an OEB Electricity Generation License. | Signature of Customer Representative (Note: Must be P. Eng licensed in Ontario) Print Name: Title: Date: Must affix P.Eng seal |
| --- | --- |
| *After signing the COVER, the customer shall submit it to Alectra’s Stations Engineer |  |

| Alectra’s COVER Coordinator has reviewed the customer’s Certified COVER document and the customer’s facility may be connected to the grid, subject to Controlling Authority’s final review. | Signature of Alectra’s COVER Coordinator Print Name: Title: Date: |
| --- | --- |
| The Alectra Utilities Stations Engineer shall forward (scan/fax) the completed document to the Controlling Authority to initiate the connection. The controlling authority will be Alectra Utilities System Control. The Stations Engineer shall contact (phone) the Controlling Authority, to notify him/her of the completed COVER. The Stations Engineer will ensure this document is placed within the Connection Agreement (CA). |  |

CONTROLLING AUTHORITY COVER ACCEPTANCE OF CONNECTION _______________________________________ ________________________________ Signature of Controlling Authority Dated

| ##### Section 7 | ##### CONFIRM ON POTENTIAL/ON LOAD CHECKS AND LIVE TEST TRIP ##### AT RATED SYSTEM VOLTAGE |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Legend: C = Confirm, W = Witness Result: P = Pass, F = Fail All Parts: N/A = Not Applicable |  | Legend | Result | Initial | Date mm/dd/yyyy | Note # |
| Are phasor readings completed and analyzed by the customer for Protection listed in Section 3? |  |  |  |  |  |  |
| Are phasor readings completed and analyzed by the customer for SCADA quantities listed in Section 4? |  |  |  |  |  |  |
| On Load SCADA Values confirmed consistent with test(s) performed in Section 4? |  |  |  |  |  |  |
| Post Energization Live Test Trip of the distribution connected generator performed in conjunction with Alectra (applicable for DG with Transfer Trip / Remote Trip). NOTE: Test will require Hydro One staff coordination |  |  |  |  |  |  |

NOTES:  (For Section 7)

| #: | Comments: | Date Action Resolved: (dd/mm/yyyy) | CustomerInitials | COVER Coordinator Concurrence |
| --- | --- | --- | --- | --- |

I/we acknowledge the completion of the COVER and the deficiencies identified in the “NOTES” section have been resolved.

Signature of Customer Representative (Note: Must be P. Eng licensed in Ontario) Print Name: Title: Date: Affix P.Eng. seal

| Alectra’s COVER Coordinator has reviewed the customer’s potential/on load checks at the rated system voltage | Signature of COVER Coordinator Print Name: Title: Date: |
| --- | --- |

| ##### Section 8 | ##### TEST SUMMARY REPORTS |
| --- | --- |

In accordance with the Distribution System Code, Appendix F, for a Generation facility of Small size (pg.13), Mid size (pg.21), and Large size (pg.28), the Customer shall, at Alectra Utilities’ request, provide Alectra with a summary of testing results, including any certificates of inspection or other applicable authorizations or approvals certifying that any of the Customer's new, modified or replacement facilities have passed the relevant tests and comply with all applicable instruments and standards referred to in the code. The Customer shall keep this information on file for a period of (7) years.

Distribution List (when all sections are completed): Alectra Customer Care Controlling Authority Customer Stations Engineer Alectra COVER Coordinator Records Management